# Section 16265A

# STATIC UNINTERRUPTIBLE POWER SUPPLY – Three Phase (20-30kVA)

- general

  - Scope

    - The Contractor shall furnish and install a three-phase continuous duty, on-line, double conversion, solid-state uninterruptible power system, hereafter referred to as the UPS.  The UPS shall operate in conjunction with the existing building electrical system to provide power conditioning, back-up and distribution for critical electrical loads.  The UPS shall consist of, as required by the project, the UPS module, battery cabinet(s), and accessory or “option” cabinet(s) for transformers, maintenance bypass, parallel tie, and distribution applications, and other features as described in this specification.

  - Related Sections

  - System Description

Standard UPS system will include a minimum of (1) rectifier, (1) inverter, (1) static bypass, (1) maintenance bypass, and (1) battery system.

    - Components:

      - Rectifier

      - Inverter

      - Sealed Lead Acid Batteries

      - Battery Charger

      - Automatic Bypass

      - User Interface Panel

      - Serial (RS-232) Communication Interface

      - Communication Card Slots (2)

      - Remote Emergency Power Off Contacts

      - Relay Output Contact (1)

      - Environmental Inputs (2)

      - Hardwired Input, Output

      - (Option) Input, Output, or Bypass Transformer Cabinet

      - (Option) External Matching Battery Cabinets

      - Maintenance Bypass Module

        - MBP internal to UPS module (standard)

        - (Option) External MBP in matching cabinet

      - (Option) SNMP/Web Adapter}

    - Modes of Operation: The UPS shall operate as an online, double-conversion UPS with the following modes:

      - Normal During the Normal or Double-conversion Mode the rectifier shall derive power as needed from the commercial AC utility or generator source and supply filtered and regulated DC power to the online inverter. The inverter shall convert the DC power to highly regulated and filtered AC power for the critical loads.

      - Battery Upon failure of the AC input source, the critical load must continue to be supplied by the inverter without switching. The inverter must obtain its power from the battery. There must be no interruption in power to the critical load upon failure or restoration of the AC input source.

      - Recharge Upon restoration of the AC input source, the rectifier/battery charger must recharge the battery. The inverter shall, without interruption of power, regulate the power to the critical load.

      - Bypass: The static bypass switch must be used for transferring the critical load to the AC utility supply without interruption and shall be rated for continuous operation. Automatic re-transfer to normal operation must also be accomplished without interruption of power to the critical load. The static bypass switch must be capable of manual operation.

      - Maintenance bypass: A wall-mountable maintenance bypass switch is available; however, in the absence of this feature, the integral maintenance bypass switch should be used. The maintenance bypass is used for supplying the load directly from the AC utility supply, while the UPS is isolated for maintenance or repair.

  - References

    - The UPS and all components shall be designed, manufactured and tested in accordance with the latest applicable standards of NEMA and UL as follows. Where a conflict arises between these documents and statements made herein, the statements in this specification shall govern.

Safety

        - IEC 62040-1-1 or EN 62040-1-1

        - EN 60950

        - UL 1778

        - Cabinets are NEMA 1 and IP20 rated.

Emission and Immunity:

        - EN 50091-2 (Emissions Class A and Harmonics)

        - EN61000-4-2,-3,-4,-5 - Slow high energy surges in input/output lines: 1 kV. line/earth, 0.5 kV line/line (IEC 61000-4-5) - Fast low energy transients in power lines: 2 kV. line/earth (IEC 61000-4-4) - Fast low energy transients (burst) in control and signal lines: 1 kV line/earth (IEC 61000-4-4) - Electrostatic discharge (ESD): 8 kV air discharge, 6 kV contact discharge (IEC 61000-4-2) - Electromagnetic field: IEC 61000-4-3 level 3

        - FCC Class A15J

    - Markings

UL, cUL

  - Submittals – for Review/approval

    - Submit one copy of a concise operation and maintenance manual.

  - Submittals – for construction

    - Submit one copy of a concise operation and maintenance manual.

  - Qualifications

    - The manufacturer of the unit shall have a minimum of forty years experience in the design, manufacture and testing of Uninterruptible Power Supplies.

    - For the equipment specified herein, the manufacturer shall be ISO 9001.

    - Provide Seismic tested equipment as follows:

- With optional bracing kit, the equipment and major components shall be suitable for and certified to meet all applicable seismic requirements of the California Building Code (CBC) through zone 4 application.

  - Regulatory Requirements

    - The UPS shall be UL labeled.

  - Delivery, Storage and Handling

    - Equipment shall be handled and stored in accordance with manufacturer’s instructions. One (1) copy of these instructions shall be included with the equipment at time of shipment.

  - Operation and Maintenance Manuals

    - Equipment operation and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets, instruction bulletins and renewal parts lists where applicable, for the complete assembly and each major component.

  - manufacturers

    - Eaton

  - Ratings

    - System Input

      - Input Voltage Operation Range

        - Nominal 208/120  or 220/127 VAC, 4-wire plus ground

        - Nominal 480 or 600 VAC available with optional input transformer in matching enclosure, 3-wire plus ground

        - +10% to –15% from nominal

- 2. Input Frequency

- a. 45 to 65 Hz

- b. auto-sensing

- c. capable of 50 to 60 Hz or 60 to 50 Hz frequency conversion

- 3. Input Power Factor: 0.99 typical

- 4. Input Current Distortion: 5% THD maximum at full rated linear load

- 5. Inrush Current:

- a. <2x branch rating without input transformer

- b. <5x branch rating with input transformer

- 6. Surge Protection:

- a. Line to Line 180J

- b. Line to Ground 450J

    - System Output, Normal Mode -Nominal Output Voltage

      - 208/120, or 220/127 VAC, Selectable through front panel or through serial port connection with power management software, (or 480 VAC with optional output isolation transformer in matching cabinet)

      - Voltage regulation: +/-2% of selected output voltage in steady state

      - Transient Voltage Response: Meets Class 1 performance of IEC62040-3; +/-5% for 100% step load change; recovery in <1ms

      - Voltage THD:

        - 2% Total Harmonic Distortion (THD) maximum phase to neutral into a maximum rated linear load (5% phase to phase)

        - 5% THD maximum phase to neutral into a maximum rated non-linear load (7% phase to phase)

      - Nominal Frequency: 50 or 60 Hz selectable

      - Frequency Regulation:

        - 50/60 Hz +/- 0.5 to +/- 3.0 Hz selectable, synchronized to mains, +/- 0.005 Hz free running single units

        - +/- 0.15 Hz parallel units

      - Slew rate:

        - selectable to 1.0, 2.0, 3.0 Hz/s for single units,

        - < 0.5 Hz/s for parallel units;

        - Generator Mode (6 / 7.5 Hz/s) for single units selectable through software parameters that can be configured via LCD and service PC interface

      - Output Current: Maximum output current (at nominal output voltage) for the UPS shall be:

        - 20 kVA system: 55 A @ 208 V, 52 A @ 220 V

        - 30 kVA system: 83 A @ 208 V, 79 A @ 220 V

      - Current Overload Capability without Bypass:

        - 125% for 1 min

        - 150% for 5 seconds

        - >150% for 300 ms

      - Current Overload Capability with Bypass enabled”

        - 1500A for ½ cycle

        - 1000A for 0.1 sec

        - 600A for 1 sec

      - Bypass:

        - Automatic bypass shall provide an alternate path to power in the case of overload, inverter failure or other UPS failure

        - External Maintenance Bypass can be utilized with the UPS to allow servicing of the UPS

        - Transfer time to and from any internal bypass shall be no-break

      - Efficiency: Typical >91% while in normal mode, with nominal line conditions

    - System Output, Battery Mode

      - Nominal Output Voltage: This shall be the user-selected output voltage

      - Voltage Regulation: +/-1% phase to neutral of selected nominal voltage (+/-2% phase to phase)

      - Transient Voltage Response

        - Meets Class 1 performance of IEC62040-3

        - +/-5% for 100% step load change; recovery in <1ms

      - Voltage THD:

        - 2% Total Harmonic Distortion (THD) maximum into a maximum rated linear load

        - 5% THD maximum phase to neutral into a maximum rated non-linear load (7% phase to phase)

      - Frequency Regulation: +/-0.005 Hz of selected nominal frequency

      - Overload Capacity:

        - 125% for 1 min

        - 150% for 5 seconds

        - >150% for 300 ms

  - construction

    - The UPS system is initially provided as a single-module, non-redundant

system. The UPS shall be field-upgradeable for power rating (20 kVA to 30 kVA), additional parallel capacity or for redundant operation. The system can be configured with numerous options, including:

      - External Matching Battery Cabinets

      - Several Connectivity Options

      - Wall-mounted Maintenance Bypass Cabinet

      - Wall-mounted Hot-tie Cabinet with Bypass

      - Matching Options Cabinet with:

        - Maintenance Bypass Switch

        - Input Transformer

        - Bypass Transformer

        - Output Transformer

    - Converter (rectifier): Incoming power shall be filtered and converted to DC by a sine-wave rectifier. The rectifier corrects the input power factor to 0.99 and draws sinusoidal current (with less than 5% THD) from the utility. In the event of utility failure, the DC-DC converter shall be supplied power without interruption from the internal or external batteries.

      - Overload Capacity: The converter shall be capable of supplying up to 150% of rated load for at least five (5) seconds if no bypass is available.

    - Inverter: The inverter utilizes IGBT technology and Digital Signal Processing to convert the DC power from the rectifier or converter to regulated AC power for output to critical loads.

      - Output Voltage: The inverter output voltage is specified in section 1.12.B.

      - Voltage Regulation: The inverter steady state voltage regulation is +/- 1% phase to neutral, 2% phase to phase. Dynamic regulation meets Class 1 performance of IEC62040-3.

      - Frequency Control: The inverter steady state frequency regulation is +/-0.005 Hz, free running in steady state. UPS is synchronized to Utility in normal operation.

    - Mechanical Construction

      - All materials and components of the UPS shall be new, of current manufacture, and shall not have been in prior service except as required during factory testing. The UPS shall be constructed of replaceable subassemblies. All active electronic devices shall be solid-state.

      - The UPS unit is comprised of an input rectifier, battery charger, inverter, bypass, and battery consisting of the appropriate number of sealed battery modules and shall be housed in a single freestanding enclosure. The UPS cabinet shall be cleaned, primed, and painted with the manufacturer's standard color. Casters and leveling feet shall be provided as standard.

      - Option Cabinets match the UPS cabinet, and may contain, input, bypass, or output transformers, and may include a rotary Maintenance Bypass Switch

      - Matching external battery cabinets shall be available in different sizes.

      - Dimensions of standard UPS and external battery or option cabinets:

Enclosure 				Dimensions (H x W x D) 	Weight (inc. bat)

UPS: 				66 x 20 x 34 inches 		1105 lbs

½ BATTERY CAB: 			66 x 20 x 31 inches 		1100 lbs

FULL BATT CAB: 			66 x 20 x 31 inches 		2060lbs

OPTION CAB MBP ONLY: 		66 x 20 x 34 inches 		205 lbs

OPT CAB W/TRANSFORMER: 	66 x 20 x 34 inches 		535 lbs

  - system input & output connections

    - AC Input:

      - All UPS units shall be capable of utilizing hardwired input. Input, Bypass, and/or output terminals may be placed in Option cabinets as determined by system configuration. Option cabinets will contain sufficient power cabling to connect to the UPS power terminals when the Option cabinets are placed adjacent to the UPS.

      - Input neutral is required for proper UPS operation unless input transformer option is used.

    - AC Output:

      - All UPS units shall be capable of utilizing hardwired output

    - Extended Battery Connector: External battery cabinets include cable to connect each battery cabinet to the UPS or daisy chain external battery cabinets.

    - Remote Emergency Power Off (REPO) Connection: The UPS shall provide a built-in landing for field connection of a Remote Emergency Power Off circuit. Upon initiation of the REPO circuit, the UPS shall open its input relays, and disengage the battery converter, preventing power from being delivered to the attached loads.

    - Serial (RS-232) Communication Interface: A 9-pin sub-D connector shall provide capability for communicating with manufacture-supplied software package. The UPS shall also provide signals for indication of UPS alarm status.

    - (2) Communication Card Slots: The UPS shall provide (2) communication X-slots in the back of the UPS allowing for additional connectivity options, including SNMP/Web, AS/400 relays, Modbus/Jbus capabilities, etc.

    - (2) Programmable Input Connections: The UPS shall provide built-in inputs for field connection (environmental input). The inputs shall be parameter programmable to suit the needs of the application.

  - User Interface

    - Front Panel Display: The UPS shall include a front panel display consisting of a graphical LCD display with backlight, four status LED’s, and a four-key keypad.

      - Graphical LCD display: Includes basic language (English and local selectable language), display of unit function and operating parameters. It shall be used to signify the operating state of the UPS, for indicating alarms, for changing operations control parameters and set points.

      - Four status LED’s, which indicate:

  - a. Alarms, with a red LED

  - b. On Battery, with a yellow LED

  - c. On Bypass, with a yellow LED

  - d. Power On, with a green LED

      - Four-Key Multifunction Keypad: UPS shall have keypad to allow user to adjust UPS parameters, view alarm and inverter logs, change UPS operational modes, and turn the UPS on and off.

    - Power Management Software Package: The UPS shall include serial communications interface that provides the following communication capabilities:

      - Monitor and graphically display input and output voltage and other operating characteristics

      - Notify end-users in the event of a power anomaly via network, E-mail or page.

      - Communication Ports:

        - Communication Card Slots: The UPS shall provide (2) communication X-slots in the back of the UPS allowing for additional connectivity options, including SNMP/Web, AS/400 relays, Modbus/Jbus capabilities, etc

        - Serial communications (via RS-232) with manufacturer-supplied power management software package

  - batteries

    - Battery Type: Valve Regulated Lead Acid (VRLA), minimum two-year warranted float service life at 25 degrees C

    - UPS Holdover Time (Runtime): Each UPS system, consisting of a minimum of six battery strings (108 battery blocks) for each power module shall have a minimum holdover time of 11 minutes, depending on kVA rating. See product manual for detailed information.

    - Extended Holdover Time (Runtime): Each UPS system shall have capability for addition of extra matching battery cabinets (in two cabinet configurations) to increase the total holdover time. Please refer to datasheet for a list of runtimes. The battery times listed are approximate and may vary depending on load configuration, temperature, battery age, and battery charge.

    - Battery Recharge Time:

      - Base UPS system consisting of six (6) battery strings will have a recharge time of max. 1.75 hours to 95% usable capacity @ nominal line after a full load discharge (30 kVA).

    - Bus Voltage: Nominal bus voltage is 216 VDC. Each string consists of 18 battery blocks in series with 9 Ah capacities.

    - Battery Protection:

      - Short Circuit Protection: Over-current protection shall protect the batteries from all short circuit fault conditions

      - Battery Module Protection: Internal battery circuit breaker shall be provided

      - Under-voltage Protection:

        - Inverter cutoff voltage: Battery operation shall be terminated when the battery voltage drops to the 1.67 VPC set point

        - Protective shutdown voltage: Inverter shall shutdown after 1 minute when the battery voltage drops below 1.7 VPC volts-per-cell typical

      - Over-voltage Protection: If the UPS system’s battery bus voltage exceeds the predetermined set point then the UPS will disable the charger and alarm a high battery condition

    - Advanced Battery Management:

      - Battery recharge: After recharging batteries to full capacity, the charger will enter the rest mode to increase the battery lifetime according the ABM cycle. Hence, continuous float charging of the battery shall not be allowed. The active battery charger states are constant-current (charge mode), constant-voltage (float mode) and no-charge (rest mode).

      - Battery Runtime Monitoring: UPS shall monitor batteries and provide status to end user of battery runtime via front panel, serial communications, or both. Runtime calculations to be based on load demand and analysis of battery health.

      - Battery Health Monitoring: UPS shall periodically test and monitor battery health and provide warnings visually, audibly and/or serially when battery capacity falls below 80% of original capacity. Battery testing may also be user initiated via front panel or serial communications.

  - nameplates

    - Provide a printed nameplate for each UPS.

  - ENVIRONMENTAL CONDITIONS

    - The UPS shall be certified to the following safety standards:

1. EN 62040-1-1, IEC 62040-1-1, EN 60950

    - The UPS shall meet CISPR22 Class A (EN50091-2) for Emissions and EN50091-2 (IEC6100032 for 16 amps or less) for Harmonics

    - Audible Noise: Less than 57 dBA (A weighted) at one (1) meter from all sides in all system modes

    - Ambient Temperature

      - Operating: UPS +5 deg C to +40 deg C

      - Storage: UPS 0 deg C to +25 deg C

    - Relative Humidity

      - Operating: 5 to 95% non-condensing.

      - Storage: 5 to 95% non-condensing.

      - There shall be at least a 1.8⁰F (1.0⁰C) difference between the dry bulb temperature and the wet bulb temperature, at all times, to maintain a noncondensing environment

      - The maximum rate of temperature change shall be limited to 3⁰F over 5 minutes

      - (36⁰F/hour), based on the ASHRAE Standard 90.1-2013

    - Altitude

      - Operating: To 1500 meters--de-rating or reducing operating temperature range may be required for higher altitudes

      - Transit: To 10,000 meters

    - Electrostatic Discharge: The UPS shall be able to withstand a minimum 8 kV without damage and without affecting the critical load

- execution

  - factory testing

    - The following standard factory tests shall be performed on the equipment provided under this section. All tests shall be in accordance with the latest version of NEMA and UL standards.

      - Standard Computer-automated UPS system test

      - Hipot test

  - installation

    - The Contractors shall install all equipment per the manufacturer’s recommendations.

  - Field Quality Control

    - Provide the services of a qualified factory-trained manufacturer’s representative to assist the Contractor in installation and start-up of the equipment specified under this section for a period of ____ working days. The manufacturer’s representative shall provide technical direction and assistance to the contractor in general assembly of the equipment, connections and adjustments, and testing of the assembly and components contained therein.

- B.  The Contractor shall provide three (3) copies of the manufacturer’s field start-up report.





