- SECTION 15000

- ADJUSTABLE FREQUENCY DRIVE EQUIPMENT – HVAC

- GENERAL

  - SCOPE

    - This specification describes the electrical, mechanical, environmental, agency and reliability requirements for three phase, adjustable frequency drives as specified herein and as shown on the contract drawings.

  - RELATED SECTIONS

  - REFERENCES

    - The adjustable frequency drives and all components shall be designed, manufactured and tested in accordance with the latest applicable standards.

      - Underwriters Laboratories (UL508C: Power Conversion     Equipment)

        - UL

        - CUL

      - National Electrical Manufacturer’s Association (NEMA)

        - ICS 7.0: Industrial Controls & Systems for AFD’s.

      - EN 61000-3-12, EN 61800-3 (1996) +A11 (2000) Category C2

        - Fulfill all EMC immunity requirements

      - Institute of Electrical and Electronic Engineers (IEEE)

        - IEEE 519-1992: Guide for harmonic content and control at the point of common coupling

    - In case of conflict between the requirements of this section and those of the listed documents, the requirements of this section shall prevail.

  - SUBMITTAL FOR REVIEW / APPROVAL

    - The following information shall be submitted to the Engineer.

      - Dimensioned outline drawing.

      - Control Schematic diagram.

      - Power and control connection diagram(s)

    - Submit  electronic copies of the above information.

  - SUBMITTAL FOR INFORMATION

    - When requested by the Engineer the following product information shall be submitted:

      - Product bulletins

      - Technical product data sheets

      - Harmonic analysis results

  - QUALIFICATIONS

    - The supplier of the assembly shall be the manufacturer of the electromechanical power components used within the assembly, such as bypass contactors, circuit breakers, and operator devices , when specified.  These Parts, when specified, shall have a commonality with other manufacturer’s products.

    - For the equipment specified herein, the manufacturer shall be ISO 9001 certified.

    - The supplier of this equipment shall have produced similar electrical equipment for a minimum period of ten (10) years.

  - REGULATORY REQUIREMENTS

  - DELIVERY, STORAGE, AND HANDLING

    - Equipment shall be handled and stored in accordance with manufacturer's instructions.  One (1) copy of these instructions shall be included with the equipment at time of shipment.

  - FIELD MEASUERMENTS

  - OPERATION AND MAINTENANCE MANUALS

    - Electronic copies of the equipment operation and maintenance manuals shall be provided.

    - Operation and maintenance manuals shall include the following information:

      - Instruction books

      - Dimensional drawings and schematics

- PRODUCTS

  - MANUFACTURERS

    - Eaton

    - _______

    - _______

Naming specific manufacturers does not imply acceptance of their standard products nor relieve them from meeting these specifications in their entirety.  Manufacturers not listed must submit a request to be considered at least 3 weeks prior to the bid date.

  - ADJUSTABLE FREQUENCY DRIVES (AFD)

    - Where shown on the drawings, adjustable frequency drives 0.50 through 800 HP shall have the following features:

      - The AFD shall provide microprocessor-based control for three-phase induction motors.  The controller’s full load output current rating shall be based on a low overload application at 40 C ambient and 1.5 - 10 kHz switching frequency with automatic switching frequency de-rating in case of overload.

      - The AFD’s shall be of the Pulse Width Modulated (PWM) design converting the utility input voltage and frequency to a variable voltage and frequency output via a two-step operation. Adjustable Current Source AFD’s are not accepted.  Insulated Gate Bipolar Transistors (IGBTs) shall be used in the inverter section.  Bipolar Junction Transistors, GTOs or SCRs are not accepted.  The AFD shall run at the above listed switching frequencies.

      - The AFD’s shall have an efficiency at full load and speed that exceeds 97%.  The efficiency shall exceed 90% at 50% speed.

      - The AFD’s shall maintain a minimum line side displacement power factor of 0.96, regardless of speed and load for VFD’s less than 75 HP.  The AFD’s shall maintain a minimum line side displacement power factor of .99, regardless of speed and load for motors greater than 75 HP.

      - The AFD’s shall have a one (1) minute overload current rating of 110% for low overload applications.

      - The AFD’s shall be capable of operating any NEMA design B squirrel cage induction motor, regardless of manufacturer, with a horsepower and current rating within the capacity of the AFD.

      - The AFD’s shall have an integral EMI/RFI filter as standard.

      - VFD must contain a circuit breaker, fused disconnect is not acceptable.

      - When requested,  harmonic calculations shall be done based on the kVA capacity, X/R ratio and the impedance of the utility transformer feeding the installation, as noted on the drawings, and the total system load.  The calculations shall be made with the point of common coupling (PCC) being the point where the utility feeds multiple customers.

      - Total harmonic distortion shall be calculated based on total demand distortion conditions as defined in IEEE 519-1992.  Copies of these calculations are to be made available upon request.  The contractor shall provide any needed information to the AFD supplier three ( 3 ) weeks prior to requiring harmonic calculations.

      - The AFD’s shall be able to start into a spinning motor.  The AFD’s shall be able to determine the motor speed in any direction and resume operation without tripping. If the motor is spinning in the reverse direction, the AFD’s shall start into the motor in the reverse direction, bring the motor to a controlled stop, and then accelerate the motor to the preset speed.

      - Standard operating conditions shall be:

- Note to Spec. Writer: Consultant to choose correct system voltage from list below

        - Incoming Power: Three-phase, 208 / 230 / 480  (+10% to -10%) and 50/60 Hz (+10 to -5%) power to a fixed potential DC bus level.

        - Frequency stability of +/-0.05% for 24 hours with voltage regulation of +/-1% of maximum rated output voltage.

        - Speed regulation of +/- 0.5% of base speed.

        - Load inertia dependent carryover ( ride through ) during utility loss.

        - Insensitive to input line rotation.

        - Humidity:  0 to 95% (non-condensing and non-corrosive).

        - Altitude:  0 to 3,300 feet ( 1000 meters ) above sea level.

        - Ambient Temperature: -10 to 40 C (VT).

        - Storage Temperature:  -40 to 70 C.

      - Control features

        - Keypad

          - Frequently accessed AFD programmable parameters shall be adjustable from a digital operator keypad located on the front of the AFD.  Keypads must use plain English words for parameters, status, and diagnostic messages.  Keypads that are difficult to read or understand are not accepted, and particularly those that use alphanumeric code and tables.  Keypads shall be adjustable for contrast with large characters easily visible in normal ambient light.

          - The AFD shall include a Hand-Off-Auto selection and an Inverter/Bypass selection.  When in “Hand” the AFD will be started and the speed will be controlled from the keypad.  When in “Off”, the AFD will be stopped.  In “Auto”, the AFD will start via an external contact closure or a communication network and the AFD speed will be controlled via an external speed reference.

          - The keypad shall have copy / paste capability.

          - Upon initial power up of the AFD, the keypad shall display a start up guide that will sequence all the necessary parameter adjustments for general start up.

          - Standard advanced programming and trouble-shooting functions shall be available by using a personal computer’s USB port and Windows™ based software.  In addition the software shall permit control and monitoring via the AFD’s RS485 port. The manufacturer shall supply a the required software.  An easily understood instruction manual and software help screens shall also be provided.  The computer software shall be used for modifying the drive setup and reviewing diagnostic and trend information as outlined in this section through  section 18.

          - The operator shall be able to scroll through the keypad menu to choose between the following:

              - Monitor

              - Parameters

              - Diagnostics

              - I/O and Hardware

              - User Settings

              - Favorites

              - Direct Access ID

        - The following setups and adjustments, at a minimum, are to be available:

          - Start command from keypad, remote or communications port

          - Speed command from keypad, remote or communications port

          - Motor direction selection

          - Maximum and minimum speed limits

          - Acceleration and deceleration times, two settable ranges

          - Critical (skip) frequency avoidance

          - Torque limit

          - Multiple attempt restart function

          - Multiple preset speeds adjustment

          - Catch a spinning motor start or normal start selection

          - Programmable analog output

        - Inputs/Outputs

          - Inputs – A minimum of six (6) programmable digital inputs, two (2) analog inputs shall be provided with the following available as a minimum:

              - Remote HOA Hand/On/Off

              - Remote forward/reverse

              - Remote preset speeds

              - Remote external fault

              - Remote fault reset

              - Process control speed reference interface,           4-20 mA DC

              - Potentiometer or process control speed reference interface, 0-10V DC

              - RS485 Programming and Operator Interface Port

          - Outputs – A minimum of two (2) programmable form C Relay outputs, (1) programmable form A Relay output, and (1) programmable analog output shall be provided, with the following available at minimum.

          - Programmable relay outputs selectable with the following available at minimum:

              - Fault

              - Run

              - Ready

              - Reversing

              - Preset Speed

              - At speed

              - Wrong Direction

              - Damper Control Relay

              - Over temperature Alarm

          - Programmable analog output signal, selectable with the following available at minimum:

              - Output frequency

              - Frequency reference

              - Motor speed

              - Output current

              - Motor torque

              - Motor power

              - Motor voltage

              - DC link voltage

              - PID controller set point value

              - PID controller output value

              - PID controller feedback value

              - PID controller error value

        - Capability of two additional expandable I/O interface cards.  Upon installation, software shall automatically identify the interface card and activate the appropriate parameters.  This should be done without adding any new software.

      - Monitoring and Displays

        - The AFD’s display shall be a multi-line graphic type window capable of displaying nine lines of text and the following thirteen (13) status indicators:

              - Run

              - Forward

              - Reverse

              - Stop

              - Ready

              - Alarm

              - Fault

              - I/O Terminal

              - Keypad

              - Fieldbus

              - Hand

              - Auto

              - Off

        - The AFD’s keypad shall be capable of displaying the following monitoring functions at a minimum and be able to monitor any nine of them on a single screen:

              - Motor Speed (RPM and %)

              - Analog Input 1

              - Analog Input 2

              - Output frequency

              - Motor current

              - Motor torque

              - Motor power (kW and %)

              - Motor voltage

              - DC-link voltage

              - Heat sink temperature

              - Motor temperature

              - Run time hours (resettable)

              - Power on hours (resettable)

              - Total megawatt hours

              - Megawatt hours (resetable)

              - Digital inputs status

              - Analog and relay outputs status

              - PID references

        - The AFD’s keypad shall be able to measure in the following units:

              - Temperature in Fahrenheit

              - Temperature in Celsius

              - PSIG

              - BAR

              - FEET

              - Inches of Water Column

              - Gallons per minute

              - Feet per minute

              - Cubic Feet per minute

              - Parts per Million

              - %

      - Protective Functions

        - The AFD shall include the following protective features at minimum:

              - Overcurrent

              - Overvoltage

              - System fault

              - Undervoltage

              - Input line supervision

              - Output phase supervision

              - Under temperature

              - Overtemperature

              - Motor stalled

              - Motor over temperature

              - Motor under load

        - The AFD shall provide ground fault protection during power-up, starting, and running.  AFD’s with no ground fault protection during running are not accepted.

      - Diagnostic Features

        - Active Faults

          - The last 10 faults shall be recorded and stored in sequential order

          - Fault name and description of fault shall be displayed on the keypad.

          - Fault or alarm display shall blink

          - Display drive data at time of fault (including date and time of occurrence)

          - In the event several faults occur simultaneously, the sequence of active faults shall be viewable.

          - During a fault, the drive must be able to identify the following:

              - Code

              - ID

              - State

              - Date

              - Time

              - Operating Time

              - Motor Current

              - Output Frequency

              - Output Voltage

              - DC-Link Voltage

              - Motor Control Status

              - Motor Temperature

              - Heat Sink Temperature

        - Fault History

          - The last 40 faults shall be recorded and stored in sequential order.

          - Display drive data (including date and time) at time of fault

      - Additional features included in the AFD’s:

        - The current withstand rating of the open VFD shall be 100,000 AIC.

        - Built in communication capability options shall include Modbus RTU, Johnson Controls Metasys N2, Bacnet MSTP,  Bacnet/IP. Modbus/TCP and expansion card communications shall include LonWorks

        - The AFD shall have a cooling fan that is field replaceable using non-screw accessibility.

        - AFD shall have conformal coated circuit boards for maximum protection of air quality conditions meeting IEC 60068-2-60 requirements.  Chemical vapors IEC 60721-3-3, unit in operation class 3C3 and mechanical particles IEC 60721-3-3, unit in operation, class 3S2.

        - AFD shall not use Electrolytic Capacitors within the power circuit and shall have a minimal maintenance free shelf life of no less than 5 years.

        - AFD shall have an active (not static V/Hz curve) energy control algorithm to ensure maximum energy savings.  AFD software shall include energy optimization algorithm.  The software algorithm shall compare output voltage to the motor load.  The output voltage is optimized to reduce the motor core losses and maintain a high enough voltage to prevent the motor from becoming unstable.

      - Enclosure

        - The AFD may be designed in a NEMA Type 1, NEMA 12, or NEMA 3R enclosure.

        - The current withstand rating of the  enclosed VFD shall be 65,000 AIC.

        - The AFD shall have complete front accessibility with easily removable assemblies.

        - Cable entry shall be top or bottom entry.

      - The AFD manufacturer shall maintain, as part of a national network, engineering service facilities within 250 miles of project to provide start-up service, emergency service calls, repair work, service contracts, maintenance and training of customer personnel.

- EXECUTION

  - EXAMINATION

  - FACTORY TESTING

    - The following standard factory tests shall be performed on the equipment provided under this section.  All tests shall be in accordance with the latest version of UL and NEMA standards.

      - All printed circuit boards shall be functionally tested via automatic test equipment prior to unit installation.

      - All final assemblies shall be tested at full load with application of line-to-line and line-to-ground bolted faults.  The AFD shall trip electronically without device failure.

      - After all tests have been performed; each AFD shall undergo a burn-in test.  The drive shall be burned in at 100% inductive or motor load without an unscheduled shutdown.

      - After the burn-in cycle is complete, each AFD shall be put through a motor load test before inspection and shipping.

    - All testing and manufacturing procedures shall be ISO 9001 certified.

  - INSTALLATION

  - FIELD QUALITY CONTROL

    - Provide the services of a qualified manufacturer's employed Field Service Engineer or authorized service representative to assist the Contractor in installation and start-up of the equipment specified under this section.  Field Service personnel shall be factory trained with periodic updates. Sales representatives will not be accepted to perform this work. The manufacturer's service representative shall provide technical direction and assistance to the Contractor in general assembly of the equipment, installation as specified in manufacturer’s installation instructions, wiring, application dependant adjustments, and verification of proper AFD operation.

    - The following minimum work shall be performed by the Contractor under the technical direction of the manufacturer's service representative.

        - Inspection and final adjustments.

        - Operational and functional checks of AFD’s.

      - The contractor shall certify that he has read the drive manufacturer’s installation instructions and has installed the AFD in accordance with those instructions.

    - The Contractor shall provide electronic copies of the manufacturer's field start-up report before final payment is made.

  - MAINTENANCE / WARRANTY SERVICE

    - Standard warranty is twenty-four (24) months from the date of shipment and covers the factory repair or replacement of the defective unit.

    - Warranty is thirty-six (36) months from date of shipment when an authorized service representative performs start up and includes parts, labor and travel time.

  - FIELD TESTING

  - TRAINING

    - The Contractor shall provide a training session for up to ____ owner's representatives for ____ normal workdays with a maximum of ____ trips at a job site location determined by the owner. Training and instruction time shall be in addition to that required for start-up service.

    - The training shall be conducted by the manufacturer's qualified representative.

    - The training program shall consist of the following:

      - Instructions on the proper operation of the equipment.

      - Instructions on the proper maintenance of the equipment.

 Note to Spec. Writer – Insert data in blanks