SECTION 26 29 13.17

# ADJUSTABLE FREQUENCY DRIVE - Microdrive (MVx <10-HP)

- GENERAL

  - SCOPE

    - This specification describes the electrical, mechanical, environmental, agency and reliability requirements for three-phase, Adjustable Frequency Drives (AFD) as specified herein and as shown on the contract drawings.

  - RELATED SECTIONS

  - REFERENCES

    - The adjustable frequency drives and all components shall be designed, manufactured and tested in accordance with the latest applicable standards of:

      - NEMA, IEEE, NEC: Design Standards

      - UL Listed

      - CUL Listed

      - CE Marked (Requires EMI Filter)

  - SUBMITTAL FOR REVIEW / APPROVAL

    - The following information shall be submitted to the Engineer.

Dimensioned outline drawing.

      - Control Schematic diagram.

      - Power and control connection diagram(s)

    - Submit four (4) copies of the above information.

  - SUBMITTAL FOR INFORMATION

    - When requested by the Engineer the following product information shall be submitted:

      - Product bulletins

      - Technical product data sheets

      - Harmonic analysis results

  - SUBMITTAL FOR CLOSE-OUT

    - The following information shall be submitted for record purposes prior to final payment.

      - Final as-built drawings and information for items listed section in 1.04.1.

      - Installation information.

  - QUALIFICATIONS

    - The supplier of the assembly shall be the manufacturer of the electromechanical power components used within the assembly, such as bypass contactors, power distribution circuit breakers, when specified. These parts, when specified, shall have a commonality with other manufacturer’s products.

    - For the equipment specified herein, the manufacturer shall be ISO 9001 certified.

    - The supplier of this equipment shall have produced similar electrical equipment for a minimum period of ten (10) years.  When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

    - Adjustable Frequency Drives shall be on the basis of Eaton Electrical MVX9000 Series for function and quality. No “Approved Equal”.

  - REGULATORY REQUIREMENTS

  - DELIVERY, STORAGE, AND HANDLING

    - Equipment shall be handled and stored in accordance with manufacturer's instructions.  One (1) copy of these instructions shall be included with the equipment at time of shipment.

  - FIELD MEASUREMENTS

  - OPERATION AND MAINTENANCE MANUALS

    - Five (5) copies of the equipment operation and maintenance manuals shall be provided.

    - Operation and maintenance manuals shall include the following information:

      - Instruction books

      - Recommended renewal parts list.

      - Drawings and information required by section 1.04.3

  - EXTRA PRODUCTS

- Products

  - manufacturers

    - Eaton

    - __________

    - __________

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

2.02	ADJUSTABLE FREQUENCY DRIVES (AFD)

    - Where shown on the drawings, adjustable frequency drives 1/4 through 10 Horsepower (HP) shall have the following features:

      - The AFD shall be rated for 380-480 Vac (optional input voltages of 90-132 Vac through 1 HP and 208-240 Vac through 7 1/2 HP). The AFD shall provide microprocessor control for three-phase induction motors. The controller’s full load output current rating shall be based on constant torque application at 50 C ambient, 40 C ambient (above 7.5 HP) and 1-15 kHz switching frequency below 50 HP and 1-10 kHz 50 HP and above to reduce motor noise and avoid increased motor losses.

      - The AFD shall be of the Pulse Width Modulated (PWM) design converting the utility input voltage and frequency to a variable voltage and frequency output via a two-step operation. Adjustable Current Source AFD are not accepted. Insulated Gate Bipolar Transistors (IGBT’s) shall be used in the inverter section. Bipolar Junction Transistors, GTO’s or SCR’s are not accepted. The AFD shall run at the above listed switching frequencies.

      - The AFD shall have an efficiency at full load and speed that exceeds 95% for AFD. The efficiency shall exceed 90% at 50% speed and load.

      - The AFD shall maintain a minimum line side displacement power factor of 0.95, regardless of speed and load.

      - The AFD shall have a one (1) minute overload current rating of 150% for constant torque applications.

      - The AFD shall be capable of operating any NEMA design B squirrel cage induction motor, regardless of manufacturer, with a horsepower and current rating within the capacity of the AFD.

      - The AFD shall have a dedicated EMI/RFI filter as an Option.

      - The AFD shall limit harmonic distortion reflected onto the utility system to voltage and current levels as defined by IEEE 519-1992 for general systems applications, by utilizing an optional 3% nominal impedance integral ac three-phase line reactor. DC link chokes are not accepted.

      - Any harmonic calculations shall be done based on the kVA capacity, X/R ratio and the impedance of the utility transformer feeding the installation, as noted on the drawings, and the total system load.  The calculations shall be made with the point of common coupling (PCC) being the point where the utility feeds multiple customers.

      - Total harmonic distortion shall be calculated under worst-case conditions in accordance with the procedure outlined in IEEE 519-1992. Copies of these calculations are to be made available upon request. The contractor shall provide any needed information to the AFD supplier three (3) weeks prior to requiring harmonic calculations.

      - Standard operating conditions shall be:

Note to Spec. Writer:

Consultant to choose correct system voltage from list below

        - Incoming Power: [Single] [Three-phase [90-132 Vac (+5% to –10%)] [208-240 Vac (+5% to –10%)] [380- 480 Vac (+10% to -10%)]50/60 Hz (+/-3 Hz) power to a fixed potential DC bus level.

        - Frequency stability of +/-0.05% for 24 hours with voltage regulation of +/-1% of maximum rated output voltage.

        - Speed regulation of +/- 0.5% of base speed.

        - Load inertia dependant carryover (ride through ) during utility loss.

        - Insensitive to input line rotation.

        - Humidity:  20% to 90% (non-condensing and non-corrosive).

        - Altitude:  0 to 3,300 feet (1000 meters) above sea level.

        - Ambient Temperature: -10 to +50 C

-10 to +40C (Above 7 1/2HP)

        - Storage Temperature:  -20 to +60 C.

      - Control Functions

        - Frequently accessed AFD programmable parameters shall be adjustable from a digital operator keypad located on the front of the AFD. The AFD shall have a 1 X 4 character line alphanumeric programmable display with status indicators. Keypads must use plain English words for parameters, status, and diagnostic messages. Alphanumeric codes and tables for keypad interface are not acceptable. Keypads shall be adjustable for contrast with large characters easily visible in normal ambient light.

        - The keypad shall have optional copy/paste capability.

        - The operator shall be able to scroll through the keypad menu to choose between the following:

          - Parameter Menu

          - Keypad Control

          - Monitoring Parameter

        - The following setups and adjustments, at a minimum, are to be available:

          - Start command from keypad, remote or communications port

          - Speed command from keypad, remote or communications port

          - Motor direction selection

          - Maximum and minimum speed limits

          - Acceleration and deceleration times, two settable ranges

          - Critical (skip) frequency avoidance

          - Torque limit

          - Multiple attempt restart function

          - Multiple preset speeds adjustment

          - Programmable analog output

      - The AFD shall have the following system interfaces:

        - Inputs – A minimum of six (6) programmable digital inputs, two (2) analog inputs and serial communications interface shall be provided with the following available as a minimum:

          - Remote manual/auto

          - Remote start/stop

          - Remote forward/reverse

          - Remote preset speeds

          - Remote external trip

          - Remote fault reset

          - Process control speed reference interface, 4-20m Adc

          - Potentiometer or process control speed reference interface, 0 –10 Vdc

          - RS-485 serial interface port

        - Outputs – A minimum of two (2) discrete programmable digital outputs, one (1) programmable open collector output, and one (1) programmable analog output shall be provided, with the following available at minimum.

          - Programmable relay outputs with one (1) set of Form C contacts for each, selectable with the following available at minimum:

              - Fault

              - Run

              - Ready

              - Reverse

              - Zero speed

              - At speed

              - Warning

              - Over-voltage

              - Under-voltage

              - Over-temperature

              - PLC output indication

        - Programmable open collector output with available 24 Vdc power supply and selectable with the following available at minimum:

          - Fault

          - Run

          - Ready

          - Reverse

          - Zero speed

          - At speed

          - Warning

          - Over-voltage

          - Under-voltage

          - Over-temperature

          - PLC output indication

        - Programmable analog output signal, selectable with the following available at minimum:

          - Output frequency

          - Output current

          - PID controller Feedback signal

          - Output power

      - Monitoring and Displays

        - The AFD display shall be an LCD type capable of displaying one (1) line of text and the following ten (10) status indicators:

          - Run

          - Forward

          - Reverse

          - Stop

          - Fault

          - Frequency Reference

          - Output Frequency

          - Output Amps

          - User Defined units

        - The AFD keypad shall be capable of displaying the following monitoring functions at a minimum:

          - Command Frequency

          - Output frequency

          - Motor Current

          - Motor voltage

          - Heat sink temperature

          - User defined unit

          - Forward Reverse Direction

      - Protective Functions

        - The AFD shall include the following protective features at minimum:

          - Over-current

          - Over-voltage

          - Under-voltage

          - Over-temperature

          - Overload Protection

          - Ground Fault

        - The AFD shall provide ground fault protection during power-up, starting, and running.  AFD with no ground fault protection during running are not accepted.

      - Diagnostic Features

        - Active Faults

          - The last active fault shall be recorded and stored in sequential order

          - Fault code displayed on the keypad.

        - Fault History

          - The last 3 faults shall be recorded and stored in sequential order.

      - Additional features included in the AFD:

        - The following indicating lights shall be provided on the keypad:

          - Run

          - Stop

          - Forward

          - Reverse

        - The current withstand rating of the drive shall be 37,000 AIC.

        - Communication card for interface with (ModBus RTU) (Devicenet) control system.

        - The AFD shall have a cooling fan.

      - Enclosure

        - The AFD shall be designed in a NEMA Type 1 enclosure.

        - The AFD shall have complete front accessibility with easily removable assemblies.

        - Cable entry shall be top entry (L1, L2, L3).

        - Cable exit shall be bottom exit (T1, T2, T3, Control).

      - The AFD manufacturer shall maintain, as part of a national network, engineering service facilities within 100 miles of project to provide start-up service, emergency service calls, repair work, service contracts, maintenance and training of customer personnel.

- EXECUTION

  - ExamINATION

  - FACTORY TESTING

    - The following standard factory tests shall be performed on the equipment provided under this section. All tests shall be in accordance with the latest version of UL and NEMA standards.

          - All printed circuit boards shall be functionally tested via automatic test equipment prior to unit installation.

          - All final assemblies shall be tested at full load with application of line-to-line and line-to-ground bolted faults. The Adjustable Frequency Drive shall trip electronically without device failure.

          - After all tests have been performed, each AFD shall undergo a burn-in test. The drive shall be burned in at 100% inductive or motor load without an unscheduled shutdown.

          - After the burn-in cycle is complete, each AFD shall be put through a motor load test before inspection and shipping.

    - The manufacturer shall provide three (3) certified copies of factory test reports.

    - All testing and manufacturing procedures shall be ISO 9001 certified.

  - insTALLATION

  - FIELD QUALITY CONTROL

    - Provide the services of a qualified manufacturer's employed Field Service Engineer or authorized service representative to assist the Contractor in installation and start-up of the equipment specified under this section.  Field Service personnel shall be factory trained with periodic updates and have experience with the same model of AFD on the job site. Sales representatives will not be accepted to perform this work. The manufacturer's service representative shall provide technical direction and assistance to the Contractor in general assembly of the equipment, installation as specified in manufacturer’s installation instructions, wiring, application dependant adjustments, and verification of proper AFD operation.

    - The Contractor under the technical direction of the manufacturer’s service representative shall perform the following minimum work.

- Inspection and final adjustments.

- Operational and functional checks of AFD and spare parts.

- The contractor shall certify that he has read the drive manufacturer’s installation instructions and has installed the AFD in accordance with those instructions.

    - The Contractor shall provide three (3) copies of the manufacturer's field start-up report before final payment is made.

3.05	MAINTENANCE/WARRANTY SERVICE

A.	Standard warranty is twenty-four (24) months from the date of shipment and covers the factory repair or replacement of the defective unit.

3.06	FIELD TESTING

- Optional field testing

      - The AFD manufacturer shall perform harmonic measurements at the point where the utility feeds multiple customers (PCC) to verify compliance with IEEE 519-1992. A report of the voltage THD and current TDD shall be sent to the engineer. The contractor shall provide labor, material, and protection as needed to access the test points. The readings shall be taken with all drives and all other loads at full load, or as close as field conditions allow.

  - tRAIINING

    - The Contractor shall provide a training session for up to ____ owner's representatives for ____ normal workdays with a maximum of ____ trips at a job site location determined by the owner. Training and instruction time shall be in addition to that required for start-up service.

    - The manufacturer’s qualified representative shall conduct the training.

    - The training program shall consist of the following:

- Instructions on the proper operation of the equipment.

- Instructions on the proper maintenance of the equipment.

 Note to Spec. Writer – Insert data in blanks

 Note to Spec. Writer – Optional

 Note to Spec. Writer – Select one

 Note to Spec. Writer – Insert data in blanks