# Product Specification Guide – Champ® PRO PVMA LED Luminaires

# SECTION 26 56 19 – LED Exterior Lighting, Area Lighting

- GENERAL

  - SCOPE

    - Furnishing, installation, and assembly of LED exterior and or area lighting fixtures for use in ordinary and or industrial locations, both outdoors and indoors.

  - REFERENCES

    - National Electrical Manufacturers Association (NEMA):

      - IP66		Ingress protection against particles and wet environments

    - Underwriters Laboratories, Inc. (UL):

      - UL1598	Luminaires

      - UL1598A	Supplemental Requirements for Luminaires for Installation on Marine Vessels

    - CSA Group

      - Canadian Electrical Code (CEC)

    - International Electrotechnical Commission (IEC):

      - 60598		Luminaires - General requirements and tests

  - SUBMITTALS - FOR REVIEW/APPROVAL

    - The following information shall be submitted to the Engineer.

      - Manufacturer’s descriptive literature and technical specifications for each product

      - Manufacturer’s product drawing (2D or 3D), when requested

      - Manufacturer’s installation and maintenance document

  - QUALIFICATIONS

    - For the equipment specified herein, the manufacturer shall be ISO 9001 certified.

    - The manufacturer of this equipment shall have produced similar electrical equipment for a minimum period of ten (10) years. When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

    - Products shall be free of defects in material and workmanship

  - REGULATORY REQUIREMENTS

    - The luminaire shall meet the following certifications:

  - NEMA and  IEC Standards

    - IP66

    - IEC 60598

  - UL Standards

    - UL1598 Luminaires

    - UL1598A Marine

  - CSA Standard

    - cUL Listed to CSA Standard CSA C22.2 No. 250

    - Additional Certifications

    - CE compliant

    - RoHS compliant

    - Design Lights Consortium approved

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer’s unopened packaging until ready for installation

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturers:

- Eaton’s Crouse-Hinds Business

- 1201 Wolf Street

- Syracuse, NY 13208

- (866) 764-5454

- www.crouse-hinds.com

- The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

  - ELECTRICAL REQUIREMENTS

    - Champ® Pro PVMA LED Luminaires:

      - Standard input driver voltage of 120-277 VAC, 50/60 Hz with optional drivers having 347-480 VAC

      - Power Factor > 0.9 @ 277VAC & THD < 20% @ 277VAC

      - Optional voltage input of 127- 300 VDC shall be available

      - System Efficiency: Each 5000 lumen and 7500 lumen models shall provide a minimum of 120 lumens per watt, using Type V optics and a clear glass lens.

      - LED fixtures shall include a 6 pole or 3 pole terminal block with clearly marked input/output for line, neutral and ground electrical connections for 120-277 VAC input range options

      - Drivers must have an L10 reliability of a minimum of 75,000 hours @ 65°C case temperature (i.e no more than 10% of drivers installed in the field may fail catastrophically in the above specified duration and temperature range)

  - material requirements

    - Champ® Pro PVMA LED Luminaires:

      - LED housing assembly and heat sink must be of die cast aluminum with epoxy powder coat for corrosion protection and heat dissipation.

      - Fixture shall have external surface of copper-free anodized aluminum and silicon type gaskets between the lens and LED board assembly, driver and LED housing for protection against acids (including acetic acid), sulfur, water (liquid and vapor form), hydrocarbons and chlorine.

      - LED board assembly lens cover must be made of heat- and impact-resistant glass. Shatterproof Teflon coating or polycarbonate material options shall be available for glass prohibited applications.

      - The LED housing shall be factory sealed.

      - Fixture must utilize silicon type gaskets between the driver and LED housing as well as the lens cover and LED board for ingress protection against dust and water

      - Fixtures must not contain mercury or any other hazardous chemicals.

      - Optional wire guard accessory must be of stainless steel.

      - Optional cone top hat must be available for applications in dusty environments.

  - design and performance requirements

    - Champ® Pro PVMA LED Luminaires:

      - Fixture must have field serviceable drivers.

      - Fixture must be available with cone shaped top hat for dust shedding.

      - Fixture must have vertical fin design at the LED housing to maximize heat dissipation and facilitate dust shedding.

      - All wiring must be concealed in the top hat and driver housing.

      - Fixture shall be total cut-off type to reduce light spill and glare.

      - Standard 6 pole or 3 pole terminal block with line, neutral and ground connections must be utilized for 120-277 VAC fixture construction.

      - Fixture must have a separate driver housing and gasket joint construction for water ingress and thermal protection.

      - Thermal grease must be utilized for heat dissipation from the PCB board.

      - Fixture shall have domed lens construction to increase optical efficiency.

      - Fixtures must have a start-up and operating ambient temperature range of -40°C to +55ºC.

      - Fixtures must have Design Lights Consortium® approval and listing for 5000 lumen and 7500 lumen models with cool white and warm white color temperatures, for both 120-277 VAC /UNV1 and 347-480VAC/ UNV34 options.

      - Lumen output, efficacy, wattage, CRI, CCT, power factor, THD, amperage, insitu temperature data and L70 lifetime must be validated from third party LM79, LM80 and TM21 calculation reports.

  - led system and optics requirements

    - Champ® Pro PVMA LED Luminaires:

      - LED fixtures must have correlated color temperature of 3000K, 4000K, 5000K, or 5700K

      - Fixtures shall use discrete OSRAM LEDs with a minimum CRI of 70 at 5000K and L70 of 400,000 at 55°C ambient temperature

      - LED fixtures must have a rated life of a minimum 60,000 hours @ operating ambient temperature of 55°C.  This must be a complete system life including life of drivers.

      - External drivers must be utilized with a minimum of 3” separation from LED PCB circuit for effective heat dissipation and increased reliability.  The drivers must be field replaceable.

      - Custom optics over each discrete LED and domed lens must be provided for maximum optical efficiency.  Refractors and reflectors should not be utilized to achieve specific optical patterns.

      - The following optional optical pattern must be made available to maximize the light distribution and intensity (lux/footcandles) for different high bay/low bay, wall, stanchion, pendant and ceiling mount applications:

        - Type V - regular circular distribution pattern for low bay indoor and outdoor ceiling or pendant mount lighting.  The LED fixture must be able to provide a coverage of >=0.72 FC over a circular area

      - The following lens options must be available with standard LED light fixture:

        - Clear glass

        - Polycarbonate to meet food/grain requirements

        - Diffused glass (non-glare)

        - Diffused Polycarbonate

- EXECUTION

  - INSTALLATION

    - The fixture must have retrofit capability with existing Eaton’s Crouse-Hinds HID and LED fixture top hats using stainless steel bolt and threaded housing for positive retention

    - The fixture shall be compatible with an optional safety clip to support the housing assembly to top hat during field installation process

    - The fixture shall mount to all Eaton Crouse-Hinds Champ VMV module top hats, including:

      - Pendant, wall, and ceiling mount options with ¾” and 1” conduit hub sizes

      - Pendant, wall, and ceiling mount options with 20mm and 25mm conduit hub sizes

      - Cone pendant with 1” and 2.75” conduit hub sizes

      - 25° and 90° stanchion mount options with 1.5”  hub size