# Product Specification Guide – Champ® VMV LED Luminaires

# SECTION 26 54 00 – Classified Location Lighting

- GENERAL

  - SCOPE

    - Furnishing, installation, and assembly of lighting fixtures for areas classified as hazardous.

  - REFERENCES

    - National Fire Protection Association (NFPA):

      - NFPA 70	National Electrical Code (NEC)

    - CSA Group

      - Canadian Electrical Code (CEC)

    - Underwriters Laboratories, Inc. (UL):

      - UL844		Luminaires for Use in Hazardous (Classified) Locations

      - UL1598	Luminaires

      - UL1598A	Supplemental Requirements for Luminaires for Installation on Marine Vessels

      - UL8750	Light Emitting Diode (LED) Equipment for Use in Lighting Products

      - UL50		Enclosures for Electrical Equipment, Non-Environmental Considerations

      - UL50E		Enclosures for Electrical Equipment, Environmental Considerations

    - National Electrical Manufacturers Association (NEMA):

    - International Electrotechnical Commission (IEC):

      - 60079		Explosive Atmospheres

      - 60529		IP Degree of Protection

      - 60598		Luminaires - General requirements and tests

    - European Commission (EU):

      - Directive 94/9/EC	Equipment for explosive atmospheres (ATEX)

  - SUBMITTALS - FOR REVIEW/APPROVAL

    - The following information shall be submitted to the Engineer.

      - Manufacturer’s descriptive literature and technical specifications for each product

      - Manufacturer’s product drawing (2D or 3D), when requested

      - Manufacturer’s installation and maintenance document

  - QUALIFICATIONS

    - The supplier of the assembly shall be the manufacturer of the major components within the assembly.

    - For the equipment specified herein, the manufacturer shall be ISO 9001 certified.

    - The manufacturer of this equipment shall have produced similar electrical equipment for a minimum period of five (5) years. When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

    - Products shall be free of defects in material and workmanship

  - REGULATORY REQUIREMENTS

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer’s unopened packaging until ready for installation

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturers:

- Eaton’s Crouse-Hinds Business

- 1201 Wolf Street

- Syracuse, NY 13208

- (866) 764-5454

- www.crouse-hinds.com

- The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

  - ELECTRICAL REQUIREMENTS

    - Champ® VMV LED Luminaires:

      - Standard input driver voltage of 100-277 VAC, 50/60 Hz with optional drivers having 347-480 VAC

      - Power factor > 0.9 @ 277 VAC & THD < 20% @ 277 VAC

      - Optional voltage input of 108-250 VDC should be available

      - System efficiency: minimum of 79 lumens per watt (LPW) for Type V optical configuration fixtures and 70 LPW for Type I and Type III optical configuration fixtures

      - LED fixtures shall include 3 or 6 pole terminal block with clearly marked input/output for line, neutral and ground electrical connections for 100-277 VAC input range options

      - Drivers must have an L10 reliability of a minimum of 60,000 hours @ 55°C ambient (i.e no more than 10% of drivers installed in the field may fail catastrophically in the above specified duration and temperature range)

      - For fixtures with lumen output > 5000 lumens, discrete LEDs must be connected in multiple series circuits by multiple drivers or power supplies to increase fixture’s overall system reliability and prevent complete loss of illumination in the event of the failure of a single driver

  - material requirements

    - Champ® VMV LED Luminaires:

      - LED housing assembly and heat sink must be of die cast aluminum with epoxy powder coat for corrosion protection and heat dissipation

      - Fixture shall have external surface of copper-free anodized aluminum and silicon type gaskets between the lens and LED board assembly, driver and LED housing for protection against acids (including acetic acid), sulfur, water (liquid and vapor form), hydrocarbons and chlorine

      - LED board assembly lens cover must be made of heat- and impact-resistant glass. Shatterproof Teflon coating or polycarbonate material options should be available for glass prohibited applications.

      - Fixture must utilize silicon type gaskets between the driver and LED housing as well as the lens cover and LED board for ingress protection against dust and water

      - Fixtures must not contain mercury or any other hazardous chemicals

      - Diffused lens option must be available for applications requiring low glare

      - Optional wire guard accessory must be of stainless steel

      - Optional cone top hat must be provided for applications in dusty environments

  - design and performance requirements

    - Champ® VMV LED Luminaires:

      - Fixture must have serviceable drivers.

      - Fixture must be available with cone shaped top hat for dust shedding

      - Fixture must have vertical fin design at the housing to maximize heat dissipation and facilitate dust shedding

      - All wiring must be concealed in the top hat and driver housing

      - Fixture shall be total cut-off type to reduce light spill and glare

      - Lever-lock connectors must be utilized for wiring connection from LEDs to drivers and from drivers to terminal block and mains

      - Standard 3 pole or 6 pole terminal block with line, neutral and ground connections must be utilized for 100-277 VAC fixture construction

      - Fixture must have a separate driver housing and gasket joint construction for water ingress and thermal protection

      - Thermal pad must be utilized instead of thermal grease for heat dissipation from PCB board

      - Optics must have ability to be clocked and preset to various positions from factory to accommodate alignment with conduit wiring entries to the fixture top hat

      - For fixtures with lumen output > 5000 lumens, fixtures must have multiple discrete LED series circuits connected to two or more drivers for redundancy and to avoid complete loss of illumination in the event of a driver failure

      - Fixture shall have domed lens construction to increase optical efficiency

      - Drivers must have a L10 reliability of a minimum of 60,000 hours @ 55°C ambient (i.e no more than 10% of drivers installed in the field may fail catastrophically in the above specified duration and temperature range)

      - Fixtures must have a start-up and operating ambient temperature range of -40°C to +55ºC

      - Water may not enter the compartment that houses wiring, wiring devices or lamps under any condition of exposure other than submersion

      - Fixtures must have DesignLights Consortium® approval and listing for cool white 100-277 VAC /UNV1 options for all lumen levels

      - Fixture shall successfully be tested for 3 axis (8G) vibration testing to withstand extreme vibration-prone environments

      - Single fixture construction meeting both NEC and IEC certifications

      - Lumen output, efficacy, wattage, CRI, CCT, power factor, THD, amperage, insitu temperature data and L70 lifetime must be validated from third party LM79, LM80 and TM21 calculation reports.

  - led system and optics requirements

    - Champ® VMV LED Luminaires:

      - LED fixtures must have correlated color temperature of 5000K or 3000K

      - Fixtures shall use discrete Luxeon M power emitters with a minimum CRI of 70 @ 5000K and L70 of 400,000 @ 55°C ambient

      - LED fixtures must have a rated life of a minimum 60,000 hours @ operating ambient temperature of 55°C.  This must be a complete system life including life of drivers.

      - External drivers must be utilized with a minimum of 3” separation from LED PCB circuit for effective heat dissipation and increased reliability.  The drivers must be field replaceable in hazardous and industrial locations.

      - Fixtures must have redundant power drivers so that loss of an individual driver does not cause complete loss of illumination

      - Custom optics over each discrete LED and domed lens must be provided for maximum optical efficiency.  Refractors and reflectors should not be utilized to achieve specific optical patterns.

      - The following optional optical patterns must be made available as options to maximize the light distribution and intensity (lux/footcandles) for different high bay/low bay, wall, pole, pendant and ceiling mount applications:

        - Type I - long and rectangular for hallways, walkways, loading docks, conveyors etc. The LED fixture must be able to provide a coverage of >= 0.58 FC over 100X40 ft. area from a min. of 18 ft. mounting height.

        - Type III - wall Mount forward throw light distribution minimizing spillover on the wall.  The LED fixture must be able to provide a coverage of >= 0.61 FC over 100X20 ft. area in front of a wall or pole mounted application from a min. of 18 ft. mounting height.

        - Type V - regular circular distribution pattern for high/low bay indoor and outdoor ceiling or pendant mount lighting.  The LED fixture must be able to provide a coverage of >=0.72 FC over a circular area with a min. of 60 ft. diameter from a min. of 18 ft. mounting height.

      - The following lens options must be available with standard LED light fixture:

        - Clear glass

        - Polycarbonate to meet food/grain requirements

        - Diffused glass (non-glare)

        - Teflon coated shatterproof glass

- EXECUTION

  - INSTALLATION

    - The fixture must have retrofit capability with existing Eaton’s Crouse-Hinds HID and LED fixture top hats using stainless steel bolt and threaded housing for positive retention

    - The fixture shall be provided with a holding clip to support the housing assembly to top hat during field installation process

    - The fixture shall mount to all existing modules in the field:

      - Pendant, wall and ceiling mount options with ¾” and 1” conduit hub size

      - 25° and 90° stanchion mount options with 1.5” and 1.5” 25 deg. hub

      - Trunnion mount with 0°, 22.5° and 45° angles.  The trunnion should not be adjustable to an angle greater than ±90° to meet temperature requirements.