# Using the SVX AOI for the 101 127 Assemblies

# Import the AOI to the CLX

Import the AOI into the project by right clicking on the Add-On-Instruction and select Import Add-On-Instruction.

Navigate to where you stored the AOIs and select the SVX_AOI_101_127 AOI  (and others if needed)

You will have a window like the one shown below, select OK

Once added the AOI will then be present in the tree.

# Import the EDS

Once the AOI is imported into the project the next step is to add the SVX to the EtherNet/IP Ethernet card.

You must first import the EDS file if you have not done this already using the Tools / EDSHardwareInstallationTool dropdown.

Right mouse click on the Ethernet icon in the tree under the scanner card and add the SVX EDS file.

To simplify finding the EDS file select only Eaton Electrical.

# Add the SVX to the CLX

Once the EDS file is added, add the SVX to the project as a new module under the Ethernet port.

Then do the typical things that need to be done when adding a device to Ethernet.  Create a unique name for the device, my example is SVX (remember this tag name, it will be used later), this is also where you select the IP address of the SVX.

Select the correct IO data assemblies, this is by selecting the Change button.  Go the next page for the graphic.

Select the arrow under the Name column to select the Asm 101 OT – 127 TO assembly.  Leave the Size as INT.   Then select OK.

At this time the device is in the project and we need to associate the AIO to the device, the next step is to link the two together so that the tags are usable in the program.

# Adding the AOI to the project

In this example under the MainRoutine we will add the SVX AOI.

On the tool bar for the logic editor there is an Add-On group, select that group and then select SVX_AOI_101_127 (hover over the AOI to identify the correct one prior to selecting).

Once selected, the AOI will appear in the rung.  In this example, the tag name of the AOI will be the same as the tag name of the SVX drive which was added to the network.   Start by naming the SVX AOI, this example will use SVX as the name(type this information into the SVX_AOI_101_127 tag name location)

Select the Input and Output, this is what creates links from  the AOI to the Device on the network.  Select the drop down, navigate to the SVX input data SVX:I1.Data, then hit the Enter key on the keyboard or click off the popup to select the tag.

You will do this for the output data as well, select the :SVX:O1.Data.

The Comms will work the same way as the Input and Output, this will be under the I1 of the device and will be the .ConnectionFaulted tag.

The last step is to add the new tag to the controller memory, this is performed by  right clicking on the SVX tag, choosing New  and adding it to the controller memory..

Lastly, in the Controller Tags you will see where the tags are created by the AOI under the Device tag you created.