How To Use the SVX Add-On Instructions

Overview

Below is a procedure on how to import an Add-On Instruction and use it in the Main Routine.

Before importing the Add-On Instruction, add the SVX Drive to the Ethernet network in RSLogix5000 using the SVX EDS file. This file can be found on the Eaton website. It is also included in the zip file with the Add-On Instruction.

The SVX Add-On Instruction provides the analog values such a Speed Actual, Speed Reference, Motor Current, Motor Voltage and so on in floating point format. This program takes care of the scaling. The Process Data Out (1-8) values assume the default assignments are used as follows.

ProcessDataOut1	Output Frequency (Hz)

ProcessDataOut2	Motor Speed (RPM)

ProcessDataOut3	Motor Current (A)

ProcessDataOut4	Motor Torque (%)

ProcessDataOut5	Motor Power (%)

ProcessDataOut6	Motor Voltage (V)

ProcessDataOut7	DC Link Voltage (V)

ProcessDataOut8	Last Active Fault Code

In addition, the Speed Actual and Speed Reference values are 0-100.00%.

Create An Ethernet/IP Network and Add the SVX Drive

In the Controller Organizer, right click on 1756 Backplane, 1756-A4 at the bottom. The Select Module Type window will open. Select the Ethernet/IP scanner being used. For this example the scanner is a 1756-ENBT. Give it a name, an IP address and be sure the revision of the module is correct.

Then, add the SVX drive to the network. If you have not registered the EDS file for the SVX drive into RSLogix5000, that must be completed before adding the SVX drive to the Ethernet/IP network. Right click on the Ethernet which is below the just added EIP Scanner and select only New Module. Then, select Eaton products as shown below:

Choose the last device shown, SVX/SPX9000 and select Create. Fill in the information for this window as shown below. Enter the IP address for your system.

Then select the Change button and fill in the next window as shown below:

Click OK and the Ethernet/IP network with the Ethernet/IP scanner and the SVX drive will be created.

Importing the Add-On Instruction

To use the SVX Add-On Instruction, open the RSLogix5000 project where it will be used.

Right click on Add-On Instructions on the Controller Organizer on the left of the screen and select Import Add-On Instruction. Locate the Add-On Instruction on your computer and select Open. The tree in RSLogix5000 should look like the following.

The parameters, tags and logic for this Add-On Instruction are available to view under SVX_AOI_111_127.

Adding the SVX Drive AOI to the MainRoutine

To add this Add-On Instruction to the MainRoutine, open the MainRoutine as shown below:

In the area above where logic is entered are all of the available instructions. Select the category called Add-On and the SVX Add-On Instruction will be displayed above, as shown below.

Select the SVX AOI to add it to your program as shown below.

Right click the ? associated with “SVX_AOI_111_127”, select ‘New Tag’ and enter a tag name, then select Create per the following. SVX is used for the Tag Name in this example. This name can be anything, but it should match the name given for this device when it was added to the Ethernet/IP network.

Be sure all fields have the selections shown above, then select Create.

Add the Input and Output addresses by selecting the ? next to each one and select the addresses as shown below. For the Comm_Status parameter, select the Connection Faulted bit that appears under Input along with the input data as shown below.

Note that the Connection_Fault tag represents a communication fault the same as Comms_Status.

The information for the Add-On Instruction will then be displayed and the instruction is now included in your logic. Specific tags were selected to be displayed in the instruction, but all I/O tags are now available to be used in the program. All the Input and Output tags are shown below. They correspond to the tag names documented in the OPTCQ Ethernet/IP Option Card User manual (publication MN04002005E) for Input assembly 127 and Output assembly 111. These tags are located in the Parameters and Local Tags area under MainProgram in the RSLogix5000 project.

The Logic area for the Add-On Instruction associates the generic I/O tags RSLogix5000 creates with the descriptive tags shown above. These generic I/O tags are created when a device is added to the Ethernet/IP network. The generic I/O tags can be found in the Controller Tags area.

The descriptive tags shown above may now be used to control and monitor the SVX Drive on Ethernet/IP.